## Summary
Summary
This spreadsheet describes SunSpec Alliance Data Models and Modbus maps.
Each spreadsheet tab describes an individual data model of one of the following types:
Id Range | Model Type
1 | Common
2 | Aggregator
010 to 019 | Network Configuration
100 series | Inverter (superseded by the 700 series)
200 series | Meter
300 series | Environmental
400 series | String Combiner
500 series | Panel
600 series | Tracker
700 series | DER
800 series | Storage
900 - 63000 | Reserved by SunSpec Alliance
64000 series | Vendor Specific
This document includes data models that are of Approved, Test, and Draft status.
Before using any of these models, please check the release status of the model in question.
Only Approved models may be SunSpec Certified.
Canonical Representation
The documentation contained in this spreadsheet is programmatically generated from SunSpec model definition files, which can be downloaded from:
https://github.com/sunspec/models
Please note that the SunSpec model definition files are the canonical (definitive) representations of SunSpec models.
SunSpec Specification Documentation
All current SunSpec specifications (PDF format) are available for free downloading at:
https://sunspec.org/sunspec-specifications/
SunSpec Certification
If you would like to have your product SunSpec Certified you can apply for Certification here:
https://sunspec.org/sunspec-certification-application/
After applying, someone from SunSpec will followup shortly.
You can also contact certification@sunspec.org to ask questions and start the process.

## 802
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | battery |  |  | group | [6 empty] | Battery Base Model
0 |  | ID | 802 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | AHRtg |  |  | uint16 |  | AHRtg_SF | Ah |  | M |  | Nameplate Charge Capacity | Nameplate charge capacity in amp-hours.
3 |  | WHRtg |  |  | uint16 |  | WHRtg_SF | Wh |  | M |  | Nameplate Energy Capacity | Nameplate energy capacity in DC watt-hours.
4 |  | WChaRteMax |  |  | uint16 |  | WChaDisChaMax_SF | W |  | M |  | Nameplate Max Charge Rate | Maximum rate of energy transfer into the storage device in DC watts.
5 |  | WDisChaRteMax |  |  | uint16 |  | WChaDisChaMax_SF | W |  | M |  | Nameplate Max Discharge Rate | Maximum rate of energy transfer out of the storage device in DC watts.
6 |  | DisChaRte |  |  | uint16 |  | DisChaRte_SF | %WHRtg |  |  |  | Self Discharge Rate | Self discharge rate. Percentage of capacity (WHRtg) discharged per day.
7 |  | SoCMax |  |  | uint16 |  | SoC_SF | %WHRtg |  |  |  | Nameplate Max SoC | Manufacturer maximum state of charge, expressed as a percentage.
8 |  | SoCMin |  |  | uint16 |  | SoC_SF | %WHRtg |  |  |  | Nameplate Min SoC | Manufacturer minimum state of charge, expressed as a percentage.
9 |  | SocRsvMax |  |  | uint16 |  | SoC_SF | %WHRtg | RW |  |  | Max Reserve Percent | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
10 |  | SoCRsvMin |  |  | uint16 |  | SoC_SF | %WHRtg | RW |  |  | Min Reserve Percent | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage.
11 |  | SoC |  |  | uint16 |  | SoC_SF | %WHRtg |  | M |  | State of Charge | State of charge, expressed as a percentage.
12 |  | DoD |  |  | uint16 |  | DoD_SF | % |  |  |  | Depth of Discharge | Depth of discharge, expressed as a percentage.
13 |  | SoH |  |  | uint16 |  | SoH_SF | % |  |  |  | State of Health | Percentage of battery life remaining.
14 |  | NCyc |  |  | uint32 | [6 empty] | Cycle Count | Number of cycles executed in the battery.
16 |  | ChaSt |  |  | enum16 | [6 empty] | Charge Status | Charge status of storage device. Enumeration.
|  | OFF | 1
|  | EMPTY | 2
|  | DISCHARGING | 3
|  | CHARGING | 4
|  | FULL | 5
|  | HOLDING | 6
|  | TESTING | 7
17 |  | LocRemCtl |  |  | enum16 |  |  |  |  | M |  | Control Mode | Battery control mode. Enumeration.
|  | REMOTE | 0
|  | LOCAL | 1
18 |  | Hb |  |  | uint16 | [6 empty] | Battery Heartbeat | Value is incremented every second with periodic resets to zero.
19 |  | CtrlHb |  |  | uint16 |  |  |  | RW |  |  | Controller Heartbeat | Value is incremented every second with periodic resets to zero.
20 |  | AlmRst |  |  | uint16 |  |  |  | RW | M |  | Alarm Reset | Used to reset any latched alarms. 1 = Reset.
21 |  | Typ |  |  | enum16 |  |  |  |  | M |  | Battery Type | Type of battery. Enumeration.
|  | NOT APPLICABLE_UNKNOWN | 0
|  | LEAD_ACID | 1
|  | NICKEL_METAL_HYDRATE | 2
|  | NICKEL_CADMIUM | 3
|  | LITHIUM_ION | 4
|  | CARBON_ZINC | 5
|  | ZINC_CHLORIDE | 6
|  | ALKALINE | 7
|  | RECHARGEABLE_ALKALINE | 8
|  | SODIUM_SULFUR | 9
|  | FLOW | 10
|  | OTHER | 99
22 |  | State |  |  | enum16 |  |  |  |  | M |  | State of the Battery Bank | State of the battery bank. Enumeration.
|  | DISCONNECTED | 1
|  | INITIALIZING | 2
|  | CONNECTED | 3
|  | STANDBY | 4
|  | SOC PROTECTION | 5
|  | SUSPENDING | 6
|  | FAULT | 99
23 |  | StateVnd |  |  | enum16 | [6 empty] | Vendor Battery Bank State | Vendor specific battery bank state. Enumeration.
24 |  | WarrDt |  |  | uint32 | [6 empty] | Warranty Date | Date the device warranty expires.
26 |  | Evt1 |  |  | bitfield32 |  |  |  |  | M |  | Battery Event 1 Bitfield | Alarms and warnings. Bit flags.
|  | COMMUNICATION_ERROR | 0
|  | OVER_TEMP_ALARM | 1
|  | OVER_TEMP_WARNING | 2
|  | UNDER_TEMP_ALARM | 3
|  | UNDER_TEMP_WARNING | 4
|  | OVER_CHARGE_CURRENT_ALARM | 5
|  | OVER_CHARGE_CURRENT_WARNING | 6
|  | OVER_DISCHARGE_CURRENT_ALARM | 7
|  | OVER_DISCHARGE_CURRENT_WARNING | 8
|  | OVER_VOLT_ALARM | 9
|  | OVER_VOLT_WARNING | 10
|  | UNDER_VOLT_ALARM | 11
|  | UNDER_VOLT_WARNING | 12
|  | UNDER_SOC_MIN_ALARM | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | OVER_SOC_MAX_ALARM | 15
|  | OVER_SOC_MAX_WARNING | 16
|  | VOLTAGE_IMBALANCE_WARNING | 17
|  | TEMPERATURE_IMBALANCE_ALARM | 18
|  | TEMPERATURE_IMBALANCE_WARNING | 19
|  | CONTACTOR_ERROR | 20
|  | FAN_ERROR | 21
|  | GROUND_FAULT | 22
|  | OPEN_DOOR_ERROR | 23
|  | CURRENT_IMBALANCE_WARNING | 24
|  | OTHER_ALARM | 25
|  | OTHER_WARNING | 26
|  | RESERVED_1 | 27
|  | CONFIGURATION_ALARM | 28
|  | CONFIGURATION_WARNING | 29
28 |  | Evt2 |  |  | bitfield32 |  |  |  |  | M |  | Battery Event 2 Bitfield | Alarms and warnings. Bit flags.
30 |  | EvtVnd1 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 1 | Vendor defined events.
32 |  | EvtVnd2 |  |  | bitfield32 |  |  |  |  | M |  | Vendor Event Bitfield 2 | Vendor defined events.
34 |  | V |  |  | uint16 |  | V_SF | V |  | M |  | External Battery Voltage | DC Bus Voltage.
35 |  | VMax |  |  | uint16 |  | V_SF | V |  |  |  | Max Battery Voltage | Instantaneous maximum battery voltage.
36 |  | VMin |  |  | uint16 |  | V_SF | V |  |  |  | Min Battery Voltage | Instantaneous minimum battery voltage.
37 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  |  |  | Max Cell Voltage | Maximum voltage for all cells in the bank.
38 |  | CellVMaxStr |  |  | uint16 | [6 empty] | Max Cell Voltage String | String containing the cell with maximum voltage.
39 |  | CellVMaxMod |  |  | uint16 | [6 empty] | Max Cell Voltage Module | Module containing the cell with maximum voltage.
40 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  |  |  | Min Cell Voltage | Minimum voltage for all cells in the bank.
41 |  | CellVMinStr |  |  | uint16 | [6 empty] | Min Cell Voltage String | String containing the cell with minimum voltage.
42 |  | CellVMinMod |  |  | uint16 | [6 empty] | Min Cell Voltage Module | Module containing the cell with minimum voltage.
43 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  |  |  | Average Cell Voltage | Average cell voltage for all cells in the bank.
44 |  | A |  |  | int16 |  | A_SF | A |  | M |  | Total DC Current | Total DC current flowing to/from the battery bank.
45 |  | AChaMax |  |  | uint16 |  | AMax_SF | A |  |  |  | Max Charge Current | Instantaneous maximum DC charge current.
46 |  | ADisChaMax |  |  | uint16 |  | AMax_SF | A |  |  |  | Max Discharge Current | Instantaneous maximum DC discharge current.
47 |  | W |  |  | int16 |  | W_SF | W |  | M |  | Total Power | Total power flowing to/from the battery bank.
48 |  | ReqInvState |  |  | enum16 | [6 empty] | Inverter State Request | Request from battery to start or stop the inverter. Enumeration.
|  | NO REQUEST | 0
|  | START | 1
|  | STOP | 2
49 |  | ReqW |  |  | int16 |  | W_SF | W |  |  |  | Battery Power Request | AC Power requested by battery.
50 |  | SetOp |  |  | enum16 |  |  |  | RW | M |  | Set Operation | Instruct the battery bank to perform an operation such as connecting. Enumeration.
|  | CONNECT | 1
|  | DISCONNECT | 2
51 |  | SetInvState |  |  | enum16 |  |  |  | RW | M |  | Set Inverter State | Set the current state of the inverter.
|  | INVERTER_STOPPED | 1
|  | INVERTER_STANDBY | 2
|  | INVERTER_STARTED | 3
52 |  | AHRtg_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for charge capacity.
53 |  | WHRtg_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for energy capacity.
54 |  | WChaDisChaMax_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for maximum charge and discharge rate.
55 |  | DisChaRte_SF |  |  | sunssf | [7 empty] | Scale factor for self discharge rate.
56 |  | SoC_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for state of charge values.
57 |  | DoD_SF |  |  | sunssf | [7 empty] | Scale factor for depth of discharge.
58 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for state of health.
59 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for DC bus voltage.
60 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage.
61 |  | A_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for DC current.
62 |  | AMax_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for instantaneous DC charge/discharge current.
63 |  | W_SF |  |  | sunssf | [7 empty] | Scale factor for AC power request.

## 805
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | lithium-ion-module |  |  | group | [6 empty] | Lithium-Ion Module Model
0 |  | ID | 805 |  | uint16 |  |  |  |  | M | S | Model ID | Model identifier
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model length
2 |  | StrIdx |  |  | uint16 |  |  |  |  | M |  | String Index | Index of the string containing the module.
3 |  | ModIdx |  |  | uint16 |  |  |  |  | M |  | Module Index | Index of the module within the string.
4 |  | NCell |  |  | uint16 |  |  |  |  | M |  | Module Cell Count | Count of all cells in the module.
5 |  | SoC |  |  | uint16 |  | SoC_SF | % |  |  |  | Module SoC | Module state of charge, expressed as a percentage.
6 |  | DoD |  |  | uint16 |  | DoD_SF | % |  |  |  | Depth of Discharge | Depth of discharge for the module.
7 |  | SoH |  |  | uint16 |  | SoH_SF | % |  |  |  | Module SoH | Module state of health, expressed as a percentage.
8 |  | NCyc |  |  | uint32 | [6 empty] | Cycle Count | Count of cycles executed.
10 |  | V |  |  | uint16 |  | V_SF | V |  | M |  | Module Voltage | Voltage of the module.
11 |  | CellVMax |  |  | uint16 |  | CellV_SF | V |  | M |  | Max Cell Voltage | Maximum voltage for all cells in the module.
12 |  | CellVMaxCell |  |  | uint16 | [6 empty] | Max Cell Voltage Cell | Cell with the maximum voltage.
13 |  | CellVMin |  |  | uint16 |  | CellV_SF | V |  | M |  | Min Cell Voltage | Minimum voltage for all cells in the module.
14 |  | CellVMinCell |  |  | uint16 | [6 empty] | Min Cell Voltage Cell | Cell with the minimum voltage.
15 |  | CellVAvg |  |  | uint16 |  | CellV_SF | V |  | M |  | Average Cell Voltage | Average voltage for all cells in the module.
16 |  | CellTmpMax |  |  | int16 |  | Tmp_SF | C |  | M |  | Max Cell Temperature | Maximum temperature for all cells in the module.
17 |  | CellTmpMaxCell |  |  | uint16 | [6 empty] | Max Cell Temperature Cell | Cell with the maximum cell temperature.
18 |  | CellTmpMin |  |  | int16 |  | Tmp_SF | C |  | M |  | Min Cell Temperature | Minimum temperature for all cells in the module.
19 |  | CellTmpMinCell |  |  | uint16 | [6 empty] | Min Cell Temperature Cell | Cell with the minimum cell temperature.
20 |  | CellTmpAvg |  |  | int16 |  | Tmp_SF | C |  | M |  | Average Cell Temperature | Average temperature for all cells in the module.
21 |  | NCellBal |  |  | uint16 | [6 empty] | Balanced Cell Count | Number of cells currently being balanced in the module.
22 |  | SN |  |  | string | 16 | [5 empty] | Serial Number | Serial number for the module.
38 |  | SoC_SF |  |  | sunssf | [7 empty] | Scale factor for module state of charge.
39 |  | SoH_SF |  |  | sunssf | [7 empty] | Scale factor for module state of health.
40 |  | DoD_SF |  |  | sunssf | [7 empty] | Scale factor for module depth of discharge.
41 |  | V_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module voltage.
42 |  | CellV_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for cell voltage.
43 |  | Tmp_SF |  |  | sunssf |  |  |  |  | M |  |  | Scale factor for module temperature.
|  | lithium-ion-module.lithium-ion-module-cell |  | 0 | group
| 0 | CellV |  |  | uint16 |  | CellV_SF | V |  | M |  | Cell Voltage | Cell terminal voltage.
| 1 | CellTmp |  |  | int16 |  | Tmp_SF | C |  | M |  | Cell Temperature | Cell temperature.
| 2 | CellSt |  |  | bitfield32 | [6 empty] | Cell Status | Status of the cell.
|  | CELL_IS_BALANCING | 0

## Spec 899
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description | Standards
|  | battery |  |  | group | [6 empty] | Battery Base Model
0 |  | ID | 899 |  | uint16 | [5 empty] | S | Model ID
1 |  | L |  |  | uint16 | [5 empty] | S | Model Length
2 |  | Rail voltage |  |  | uint16 |  |  | V
3 |  | FET temperatures |  |  | uint16 |  |  | C
4 |  | AFE die temperature |  |  | uint16 |  |  | C
5 |  | MCU die temperature |  |  | uint16 |  |  | C
6 |  | DCDC temperature |  |  | uint16 |  |  | C
7 |  | Neg bat temp 1 |  |  | uint16 |  |  | C
8 |  | Neg bat temp 2 |  |  | uint16 |  |  | C
9 |  | Pos bat temp 1 (CB) |  |  | uint16 |  |  | C
10 |  | Pos terminal temp |  |  | uint16 |  |  | C
11 |  | Negative terminal temp |  |  | uint16 |  |  | C
12 |  | MAC address of ESP32 |  |  | Text 12 char
13 |  | Spec 899 protocol version |  |  | uint16
14 |  | Firmware version conroller |  |  | uint16
15 |  | Firmware version BMS |  |  | uint16
16 |  | Lifetime |  |  | uint16 |  |  | h
17 |  | SVR Accelerometer X axis |  |  | uint16 |  |  | m/s2
18 |  | SVR Accelerometer Y axis |  |  | uint16 |  |  | m/s2
19 |  | SVR Accelerometer Z axis |  |  | uint16 |  |  | m/s2
20 |  | Product ID |  |  | Text 24 char
21 |  | Hardware revision |  |  | Text 4 char
22 |  | Product name |  |  | Text 24 char
23 |  | Production date |  |  | Text 8 char
24 |  | Customer serial number |  |  | Text 24 char
25 |  | Market name |  |  | Text 24 char
26 |  | Installation date |  |  | Text 8 char
27 |  | Operation mode |  |  | bitfield32 | [7 empty] | Charge status of storage device. Enumeration.
|  | Standby Mode | 1 | [9 empty] | 1.Standby Mode Condition: No alarms; BMS is ready to close the MOSFETs. State: System is idle but can transition into active operation.
|  | Run Mode | 2 | [9 empty] | 2.Run Mode Condition: No alarms; MOSFETs are closed. State: Battery is actively operating normally.
|  | Alarm Mode | 3 | [9 empty] | 3.Alarm Mode Condition: BMS is in an alarm state; charge and discharge MOSFETs are open.State: System is stopped due to a fault or abnormal condition.
|  | Charge Disabled Mode | 4 | [9 empty] | 4.Charge Disabled Mode Condition: Charge MOSFETs are open, DC/DC is off, discharge MOSFETs are closed. State: Charging is blocked, but discharging is allowed.
|  | Charge DC/DC Mode | 5 | [9 empty] | 5.Charge DC/DC Mode Condition: Charge MOSFETs are open or DC/DC is on, discharge MOSFETs are closed.State: Battery is actively charging.
|  | Discharge Disabled Mode | 6 | [9 empty] | 6.Discharge Disabled Mode Condition: Discharge MOSFETs are open; charge MOSFETs are closed or DC/DC is running. State: Discharging is blocked, but charging is allowed.
|  | Emergency Mode | 7 | [9 empty] | 7.Emergency Mode Condition: BMS is in alarm mode and has tripped the MCB (Miniature Circuit Breaker). State: System is in critical failure mode, requiring manual intervention.
28 |  | Alarms |  |  | bitfield32 | [7 empty] | Alarms and warnings. Bit flags.
|  | Cell over temperature charge | 0
|  | Cell Over Temperature Discharge (COTD) | 1
|  | Cell Under Temperature Charge (CUTC) | 2
|  | Cell Under Temperature Discharge (CUTD) | 3
|  | System Lock | 4
|  | Short Circuit Detection | 5
|  | MOSFET Over Temperature | 6
|  | DC/DC Over Temperature | 7
|  | Current Measurement Comparison (CMC) | 8
|  | Battery Voltage Plausibility Check (BVP) | 9
|  | Cell Temperature Difference (CTD) | 10
|  | MCB trip | 11
|  | Unexpected Current Measurement (UCM) | 12
|  | External Watchdog | 13
|  | UNDER_SOC_MIN_WARNING | 14
|  | Cell under voltage Critical | 15
|  | Reserved | 16
|  | Reserved | 17
|  | Reserved | 18
|  | Reserved | 19
|  | Reserved | 20
|  | Reserved | 21
|  | Reserved | 22
|  | Reserved | 23
|  | Reserved | 24
|  | Reserved | 25
|  | Reserved | 26
|  | Reserved | 27
|  | Reserved | 28
|  | Reserved | 29